INSTRUCTION MANUAL

Duct type ozone sensor

JXBS-3005-O3

VER1.0

WeihaiJXCTElectronicTechnologyCo.,Ltd.

Ⅰ Brief Introduction

1.1 Product Overview

Ducted ozone sensors are specifically designed for plug-in pipe gas measurement. The stainless steel air duct and stainless steel flange are used as the plug-in structure, and the professional test ozone concentration sensor probe is used as the core detection device; it has a wide measurement range, high accuracy, good linearity, good versatility, convenient use, convenient installation and transmission Long distance and moderate price.

1.2 Primary Parameters

TABLE 1   Primary Parameters

| PARAMETERS | TECHNICAL SPECIFICATIONS |
| --- | --- |
| MEASURING RANGE | 0-20ppm/0-100ppm |
| MEASURING MODE | Electrochemical sensor |
| PRECISION | 3%F.s |
| RESPONSE TIME | less than 15 seconds |
| WARRANTY PERIOD | 2 years ( Host ) / 1 year ( Sensor ) |
| COMMUNICATION PORT | Analog (voltage / current) / digital (RS485) |
| POWER SUPPLY | 12-24V DC |
| POWER CONSUMPTION | ≤1W |
| OPERATING TEMPERATURE | -30-50 ℃(-20-40℃ continued) |
| WORKING HUMIDITY ENVIRONMENT | 0-100%RH(15-95%RH） |
| DUCT LENGTH | 200mm |
| CASE SIZE | 110 x 85 x 44mm3 |

1.3 Probe Parameters And Selection

| NO. | MANUFACTURER | RANGE | RESOLUTION | LIFE |
| --- | --- | --- | --- | --- |
| 20P | Domestic electrochemical probe | 20ppm | 200ppb | >2 years |
| 20PL | SPEC | 20ppm | 100ppb | >2 years |
| 20PE | HONEYWELL | 100ppm | 20ppb | >2 years |
| 01PB | Domestic semiconductor | 1000ppb | 10ppb | >2 years |

The above life is the reference value in the case of temperature 23 ± 3 ℃, humidity 40 ± 10% RH, and concentration <5%

1.4 Analog communication parameters

| Parameter | Index |
| --- | --- |
| Current output type | 4-20mA |
| Current output load | ≤600Ω |
| Voltage output type | 0-5V/0-10V |
| Voltage output load | ≤250Ω |

1.6 Digital communication parameters

| Parameter | Index |
| --- | --- |
| Communication Interface | RS485 |
| Baud rate | 2400/4800/9600 |
| Protocol | Modbus RTU |

Ⅱ Hardware Connections

2.1 CHECKING BEFORE INSTALLATION

Check the list of devices before installation:

TABLE 3   List of Devices

| Name | Number |
| --- | --- |
| THE SENSOR DEVICE | 1 |
| 12V POWER ADAPTER（Optional） | 1 |
| THE USB TO 485 DEVICE（Optional） | 1 |
| WARRANTY CARD / CERTIFICATE | 1 |

2.2 Interface Description

The power interface is wide voltage power input 12-24V. When wiring the 485 signal line, pay attention that the two A / B lines cannot be reversed, and the addresses between multiple devices on the bus must not conflict.

|  | Line Color |  | Description |
| --- | --- | --- | --- |
| Power | Brown |  | Power supply Positive ( 12-24V DC ) |
|  | Black |  | Power supply Negative |
| Communication | Yellow ( Gray ) |  | 485-A |
|  | Blue |  | 485-B |

The power interface is wide voltage power input 12-24V. For analog products, pay attention to the positive and negative signal lines. Do not reverse the positive / negative current / voltage signal lines.

|  | Line Color |  | Description |
| --- | --- | --- | --- |
| Power | Brown |  | Power supply Positive ( 12-24V DC ) |
|  | Black |  | Power supply Negative |
| Communication | Yellow ( Gray ) |  | Positive voltage / current output |
|  | Blue |  | Voltage / current output negative |

We provide default cable length of 0.6 meters, you can extend the cable yourself according to your needs.

2.3 Installation Description

The diameter of the duct of the duct sensor is 25mm. The duct sensor is delivered with a set of mounting flanges for fixing to the designated equipment pipe wall. The flanges are fixed by three 3.5mm mounting screw holes. Customers can use 3mm bolts or 3mm self-tapping screws to install according to the situation

There are screws with a distance of 105mm on the sensor housing, which can also be fixed by the fixing screws here.

The following figure shows the installation diagram of the flange. After fixing the flange, the customer can use the screws on the flange post to fix the sensor.

The following figure shows the installed reference style. The specific installation forms are various. Customers can choose a reasonable installation method according to the site conditions:

Ⅲ Digital sensor communication protocol

3.1 Communication Basic Parameters

| PARAMETERS | CONTENT |
| --- | --- |
| Protocol | Modbus RTU |
| Data bits | 8 bit |
| Parity bit | No |
| Stop bit | 1 bit |
| Error checking | CRC (redundant loop code) |
| Baud rate | 2400 bps/ 4800 bps/ 9600 bps can be set factory defaults to 9600 bps |

3.2 Data frame format definition

Modbus-RTU communication protocol is adopted, the format is as follows:

Time for initial structure ≥ 4 bytes

Address code = 1 byte

Function code = 1 byte

Data area = N bytes

Error check = 16-bit CRC

Time to end structure ≥ 4 bytes

Address code: It is the address of the transmitter and is unique in the communication network (factory default 0x01).

Function code: The function instruction of the command issued by the host, this transmitter only uses the function code 0x03 (reading register data).

Data area: The data area is the specific communication data. Note that the high byte of the 16bits data comes first!

CRC code: two-byte check code.

Inquiry frame

| address code | function code | Register start address | Register length | Low check bit | Check code high |
| --- | --- | --- | --- | --- | --- |
| 1 byte | 1 byte | 2 bytes | 2 bytes | 1 byte | 1 byte |

Response frame

| address code | function code | Number of valid bytes | Data area | Second data area | Nth data area |
| --- | --- | --- | --- | --- | --- |
| 1 byte | 1 byte | 1 byte | 2 bytes | 2 bytes | 2 bytes |

3.3 Register Address

| Register Address | Plc Configuration Address | Content | Operation |
| --- | --- | --- | --- |
| 0000H | 40001 | Humidity ( Unit 0.1%RH) | Read-Only |
| 0001H | 40002 | Temperature ( Unit 0.1℃) | Read-Only |
| 0006H | 40007 | Ozone ( unit 0.1ppm) | Read-Only |
| 0100H | 40101 | Device Address (0-252) | R/W |
| 0101H | 40102 | Baud Rate (2400/4800/9600) | R/W |

3.4 Communication protocol examples and explanations

3.4.1 Read Device Address 0x01's Ozone Concentration

Inquiry Frame

| Address Code | Function Code | Start Address | Data Length | CRC_L | CRC_H |
| --- | --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x00 0x06 | 0x00 0x01 | 0x64 | 0x0B |

Answer Frames( For example, the reading is 18.9ppm )

| Address Code | Function Code | Returns to The Number Of Valid Bytes | Ozone Value | Check Digit Low | Check Digit High |
| --- | --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x02 | 0x00 0xBD | 0x78 | 0x35 |

Ozone：

0xBD H ( hexadecimal ) =189=>Ozone=18.9ppm

3.4.2 Read Device Address 0x01's Temperature And Humidity Value

Inquiry Frame

| Address Code | Function Code | Start Address | Data Length | CRC_L | CRC_H |
| --- | --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x00,0x00 | 0x00,0x02 | 0xC4 | 0x0B |

Answer Frame(For example, read that the temperature is -10.1 ℃ and the humidity is 65.8% RH)

| Address Code | Function Code | Number Of Valid Bytes | Humidity Value | Temperature Value | CRC_L | CRC_H |
| --- | --- | --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x04 | 0x02 0x92 | 0xFF 0x9B | 0x5A | 0x3D |

Temperature：

When the temperature is lower than 0 ℃, upload it in two's complement form

FF9BH ( hexadecimal ) =-101=> Temperature =-10.1 ℃

Humidity：

0292H ( hexadecimal ) =658=> Humidity =65.8%RH

3.4.3 Read Device Address 0x01's Temperature And Humidity, Ozone Concentration Value

Inquiry Frame

| Address Code | Function Code | Start Address | Data Length | CRC_L | CRC_H |
| --- | --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x00,0x00 | 0x00,0x07 | 0x04 | 0x08 |

Answer Frame(E.g. read O3 value is 4ppm)

| Address Code | Function Code | Number Of Valid Bytes | Humidity Value | Temperature Value |
| --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x0E | 0x03 0x14 | 0x01 0x1B |
| 8 Useless Bytes |  | Ozone Value | CRC_L | CRC_H |
| 0x00 ... |  | 0x00 0x28 | 0x50 | 0x3B |

Temperature：

011B H ( hexadecimal ) =283=> Temperature =28.3 ℃

Humidity：

0314 H ( hexadecimal ) =788=> Humidity =78.8%RH

Ozone：

0028 H ( hexadecimal ) =40=> Ozone =4ppm

3.5 O3 measurement unit ppm and μg / m3 conversion

According to the calculation, the conversion relationship can be obtained, which is only valid for O3:

1ppm =48/22.4=2.143mg / m3 =2143μg / m3

1ppb =48/22.4=2.143μg / m3

IV Meaning and Conversion of Analog Sensor Parameters

4.1 Analog 4-20mA Current Output

| Current Value | O3 |
| --- | --- |
| 4mA | 0ppm |
| 20mA | 20ppm |

The formula is P（O3） = (I (current) -4mA) *1.25ppm

The unit of P is ppm and the unit of I is mA.

For example, the data collected in the current situation is 8.125mA, and the value of O3 is calculated at the maximum range of 5.15ppm.

4.2 Analogue 0-10V Voltage Output

| Voltage Value | O3 |
| --- | --- |
| 0V | 0ppm |
| 10V | 20ppm |

The formula is P（O3） = V (voltage) /500ppm

The unit of P is ppm and the unit of V is mV.

For example, the data collected in the current situation is 3515mV, and the value of O3 calculated at this time is 7.03ppm.

4.3 Analogue 0-5V voltage output

| Voltage Value | O3 |
| --- | --- |
| 0V | 0ppm |
| 5V | 20ppm |

The formula is P（O3）=V(voltage)/250ppm

The unit of P is ppm and the unit of V is mV.

For example, the data collected in the current situation is 4228mV, and the calculated value of O3 is 16.91ppm.

V Frequently Asked Questions and Quality Assurance

5.1 Digital devices cannot be connected to a PLC or computer

The possible reasons are as follows:

● The computer has multiple COM ports, and the selected port is incorrect.

● The device address is wrong, or there are devices with duplicate addresses (the factory defaults are all 1).

● Baud rate, check mode, data bit, stop bit error.

● The host polling interval and waiting for response time are too short, both need to be set above 200ms.

● The 485 bus is disconnected, or the A and B wires are reversed.

● Too many devices or wiring is too long, you should supply power nearby, add 485 booster, and increase 120Ω terminal resistance.

 ● The USB to 485 driver is not installed or damaged.

 ● Equipment is damaged.

5.2 Possible Causes of No Analog Output or Output Error

● The measurement error caused by the wrong range corresponds to the PLC calculation. Please refer to the technical specifications in Part I for the range.

● The wiring method is incorrect or the wiring sequence is wrong.

● The distance between the transmitter and the collector is too long, causing signal disturbance.

● The PLC acquisition port is damaged.

● Equipment is damaged.

5.3 Warranty and after sales

The warranty terms are in accordance with the sensor after-sales clauses of Weihai Jingxun Changtong Electronic Technology Co., Ltd. The warranty period is two years for the main circuit of the sensor, one year for the gas-sensitive probe, and three months for the accessories (shell, plug, cable, etc.)