Explosion-proof Combustible Gas Sensor

Operation Instruction

JXBS-4001-LEL_Type 485

Ver1.0

INSTRUCTION MANUAL

CHAPTER 1 Product Introduction

  - Product Overview

The explosion-proof combustible gas sensor is specially developed for some harsh environments. Cast aluminum explosion-proof shell, the probe is placed in a special metal probe bin, and the electrical part is isolated from the probe.

Combustible gas sensor adopts professional combustible gas concentration sensor probe as the core detection device; It has the characteristics of wide measuring range, high precision, good linearity, good universality, convenient use, easy installation, long transmission distance and moderate price.

  - Functional Characteristics

This product adopts high-sensitivity gas detection probe with stable signal, high precision and long quick response life.   It has the characteristics of wide measuring range,  good  linearity, convenient use, convenient installation and long transmission distance. Note that the sensor is used for air detection, and the customer should test it in the application environment to ensure that the sensor meets the requirements.

  - Product Parameter

| parameter | Technical indicators |
| --- | --- |
| LEL measurement range | 0-100%LEL |
| Measurement method | Catalytic combustion type |
| Response time | Less than 20 seconds |
| Measurement accuracy | 3%F.s |
| Interface form | Quantity (RS485) |
| Power supply | 12V-24VDC |
| Consume too much electricity | <1W |
| Operating temperature | -30-50℃(-20-40℃ continuous) |
| Working humidity | 0-100%RH(15-95%RH) |
| Environment outline | dimension explosive-proof |

| gas | lower explosive limit | LEL concentr ation | gas | lower explos ive limit |
| --- | --- | --- | --- | --- |
| metha ne | 5.0% | 100% | methane | 5.0% |
| propa ne | 2.1% | 100% | propane | 2.1% |
| * Hydr ogen | 4.1% | 100% | * Hydrogen | 4.1% |

* This product does not have hydrogen explosion lower limit detection by default.

CHAPTER 2 Hardware Connection

  - Equipment Pre-installation Inspection

Please check the equipment list before installing the equipment:

| name | quantity |
| --- | --- |
| Explosion-proof sensor | 1 set |
| 12V waterproof power supply | 1 set (optional) |
| USB to 485 device | 1 set (optional) |
| Warranty card/certificate | 1 copy |

  - Interface Description

Wide voltage power input can be 12-24V. 85 Pay attention to the fact that the A/B lines can't be reversed when connecting the signal lines, and the addresses of multiple devices  on  the bus can't conflict.

|  | Line color | explain |
| --- | --- | --- |
| Pow er S uppl y | brown | Positive power supply (12-24VDC) |
|  | black | Negative power supply |
| com mun icati on | Yellow (grey) color | 485-A |
|  | blue | 485-B |

By default, 0.85-meter-long wire rod is provided at the factory, and customers can extend the wire rod or connect the wires in sequence as needed.

  - Installation Instructions

The explosion-proof sensor is wall-mounted and can be fixed by three 8.5MM fixing holes. Customers can fix it with expansion screws or bolts. The size and position of fixing holes are as follows:

Please ensure the installation direction when  installing, and the gas inlet of the gas bin is installed vertically downward.

Figure 1. Dimensions of non-digital display acousto-optic sensor

Figure 2. Digital display sensor size

Figure 3. Dimensions of acousto-optic sensor

Figure 4. Dimensions of acousto-optic digital display sensor

CHAPTER 3 Configure Software Installation and Use

Our company provides supporting "sensor monitoring software", which can easily read the parameters of the sensor by computer and flexibly modify the device ID and address of the sensor.

  - Sensor Access to Computer

After the sensor is properly connected to the computer through USB 485 and supplied with power, you can see the correct COM port in the computer (see the COM port in "My

Computer-Properties-Device Manager-Port").

As shown in the figure above, your serial port number is COM10 at this time. Please remember this serial port, which needs to be filled in the sensor monitoring software.

If the COM port is not found in the device manager, it means that you have not inserted USB 485 or installed the driver correctly. Please contact  the technician for help.

  - Use of Sensor Monitoring Software

The software interface is shown in the figure:

After opening the software, first select the "sensor type" at the top of the software, then get the serial port number and select the correct serial port according to the method in Section 3.1, and  then click "Automatically get the current baud rate and address" to automatically detect all devices and baud rates on the current 485 bus. Please note,It is necessary to ensure that there is only one sensor on the 485 bus when using software for automatic acquisition. Then click "Connect Device" to get the sensor data information in real time.

  - Modify Baud Rate and Device Address

When the "device connection" is disconnected, click "Modify baud rate and modify slave station number"  in "Configure sensor communication parameters" to complete relevant settings. Please pay attention to restart the device after setting, and then

"Automatically get the current baud rate and  address" to find that the address and baud rate have been changed to the address and baud rate you need.

CHAPTER 4 Communication Protocol

  - Basic Communication Parameters

| parameter | content |
| --- | --- |
| encode | 8-bit binary |
| data bit | 8 bits |
| parity | without |
| Stop bit | 1 bit |
| Error calibration | CRC redundant cyclic code |
| Baud rate | 200 bps/4800 bps/9600bps can be set, and the factory default is 9600 bps. |

  - Data Frame Format Definition

Modbus-RTU communication protocol is adopted in the following format:

Initial structure > =4 bytes time Address code =1 byte

Function code =1 byte Area =N bytes

Error check =16-bit CRC code End structure > =4 bytes time

Address code: the address of the transmitter, unique in the communication network (factory default 0x01).

Function code: the instruction from the host indicates that this transmitter only uses function code 0x03 (reading meory data).

Data area: the data area is the specific communication data area, and note that the high byte of 16bits data comes first.

CRC code: Two-byte check code. Inquiry frame

| address code | function code | register start address | Register length | check code low post | check code high position |
| --- | --- | --- | --- | --- | --- |
| 1 byte | 1 byte | 2 bytes | 2 bytes | 1 byte | 1 byte |

Response frame

| address code | function code | Effective number of bytes | Data zone 1 | second data field | Nth data field |
| --- | --- | --- | --- | --- | --- |
| 1 byte | 1 byte | 1 byte | 2 bytes | 2 bytes | 2 bytes |

  - Register Address

| Register address | PLC configu ration address | content | operate |
| --- | --- | --- | --- |
| 0006H | 40007 | Combustible gas concentration (0.1ppm) | read only |
| 0100H | 40101 | Equipment address (0-252) | read and write |
| 0101H | 40102 | Baud rate (2400/4800/9600) | read and write |

  - Examples and Explanations of Communication protocols

  - Read the LEL Value of Device Address 0x01

Inquiry frame

| addres s code | functi on code | start address | Data length | Low bit check code | High bit check code |
| --- | --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x00,0x06 | 0x00,0x01 | 0x64 | 0x0B |

Response frame

| addres s code | functio n code | Effective number of bytes | LEL value | check code low post | check code high position |
| --- | --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x02 | 0x00 0xBD | 0x78 | 0x35 |

LEL：

00BD H (hexadecimal) =189=>LEL=18.9%

  - Conversion Between ppm of LEL Measurement Unit and ug/m3

According to the calculation, we can get the conversion relationship, which is only valid for LEL:

1ppm = 46/22.4=2.05mg/m3=2050ug/m3

1ppb = 46/22.4=2.05ug/m3

The	above	calculations	are	all	aimed	at	the	standard atmospheric pressure.